## Overall Design
Region | Description | State Point | T [C] | P [kPa] | s [kJ/kg] | h [kJ/kg] | φ [kJ/kg] | x [-] | Salinity [g/kg] | Notes
Nuclear Reactor | Reactor-side leaving steam gen | 10 | 275 | 15000 | 2.995 | 1208 | 1070
| Primary pump, Ideal | 11 | 275.2 | 15750 | 2.995 | 1209 | 1071
| Primary pump, Real | 12 | 275.3 | 15750 | 2.995 | 1209 | 1071
| Reactor-side entering steam gen | 13 | 320 | 15750 | 3.422 | 1453 | 1306
Interloop (electricity generation) | Interloop-side leaving condenser | 20 | 99.97 | 101.3 | 1.307 | 419.1 | 314.8 | 0
| Feed pump, Ideal | 21 | 100.1 | 2533 | 1.307 | 421.6 | 317.4
| Feed pump, Ideal | 22 | 100.2 | 2533 | 1.308 | 422 | 317.8
| Interloop-side leaving steam gen | 23 | 239.7 | 2533 | 6.345 | 2849 | 2645
| Turbine, Ideal | 24 | 99.97 | 101.3 | 6.345 | 2299 | 2094 | 0.833
| Turbine, Real | 25 | 99.97 | 101.3 | 6.492 | 2354 | 2146 | 0.8574

## MED
Region | Description | State Point | T [C] | P [kPa] | s [kJ/kg] | h [kJ/kg] | φ [kJ/kg] | x [-] | Salinity [g/kg]
Effect No.1 | Evaporator, Hot In (NPP-side) | 25 | 99.97 | 101.3 | 6.492 | 2354 | 2146 | 0.8574
| Evaporator, Hot Out (NPP-side) | 26 | 99.97 | 101.3 | 2.293 | 786.9 | 663 | 0.163
| Economizer, Hot Out (NPP-side) | 27 | 99.97 | 101.3 | 1.307 | 419.1 | 314.8 | 0
| Seawater Intake | 30 | 20 | 101.3 | 0.2965 | 84.01 | 0 |  | 35
| Economizer, Cold Out | 31 | 94.97 | 101.3 | 1.25 | 398 | 294.9 |  | 35
| Evaporator, Freshwater Steam Out | 32 | 94.97 | 84.53 | 7.415 | 2668 | 2441 | 1 | 0
| Evaporator, Brine Out | 33 | 96.39 | 84.53 | 1.266 | 403.9 | 300.5 | 0 | 85
Effect No.1 | Evaporator, Hot In | 40 | 94.97 | 84.53 | 7.415 | 2668 | 2441 | 1 | 0
| Evaporator, Hot Out | 41 | 94.97 | 84.53 | 2.353 | 803.9 | 678.7 | 0.1788 | 0
| Economizer, Hot Out | 42 | 94.97 | 84.53 | 1.25 | 398 | 294.9 | 0 | 0
| Economizer, Cold In | 43 | 20 | 101.3 | 0.2965 | 84.01 | 0 |  | 35
| Economizer, Cold Out | 44 | 89.97 | 101.3 | 1.193 | 377 | 275 |  | 35
| Evaporator, Freshwater Steam Out | 45 | 89.97 | 70.11 | 7.478 | 2660 | 2432 | 1 | 0
| Evaporator, Brine Out | 46 | 91.39 | 70.11 | 1.209 | 382.9 | 280.6 | 0 | 85
Effect No.3 | Evaporator, Hot In | 50 | 89.97 | 70.11 | 7.478 | 2660 | 2432 | 1 | 0
| Evaporator, Hot Out | 51 | 89.97 | 70.11 | 2.245 | 759 | 636 | 0.1674 | 0
| Economizer, Hot Out | 52 | 89.97 | 70.11 | 1.193 | 376.9 | 275 | 0 | 0
| Economizer, Cold In | 53 | 20 | 101.3 | 0.2965 | 84.01 | 0 |  | 35
| Economizer, Cold Out | 54 | 84.97 | 101.3 | 1.134 | 355.9 | 255.2 |  | 35
| Evaporator, Freshwater Steam Out | 55 | 84.97 | 57.81 | 7.544 | 2651 | 2422 | 1 | 0
| Evaporator, Brine Out | 56 | 86.39 | 57.81 | 1.151 | 361.9 | 260.8 | 0 | 85
Effect No.4 | Evaporator, Hot In | 60 | 84.97 | 57.81 | 7.544 | 2651 | 2422 | 1 | 0
| Evaporator, Hot Out | 61 | 84.97 | 57.81 | 2.133 | 713.4 | 592.7 | 0.1558 | 0
| Economizer, Hot Out | 62 | 84.97 | 57.81 | 1.134 | 355.9 | 255.1 | 0 | 0
| Economizer, Cold In | 63 | 20 | 101.3 | 0.2965 | 84.01 | 0 |  | 35
| Economizer, Cold Out | 64 | 79.97 | 101.3 | 1.075 | 334.9 | 235.4 |  | 35
| Evaporator, Freshwater Steam Out | 65 | 79.97 | 47.37 | 7.611 | 2643 | 2413 | 1 | 0
| Evaporator, Brine Out | 66 | 81.39 | 47.37 | 1.092 | 340.8 | 240.9 | 0 | 85
Effect No.5 | Evaporator, Hot In | 70 | 79.97 | 47.37 | 7.611 | 2643 | 2413 | 1 | 0
| Evaporator, Hot Out | 71 | 79.97 | 47.37 | 2.016 | 667.2 | 548.8 | 0.144 | 0
| Economizer, Hot Out | 72 | 79.97 | 47.37 | 1.075 | 334.9 | 235.3 | 0 | 0
| Economizer, Cold In | 73 | 20 | 101.3 | 0.2965 | 84.01 | 0 |  | 35
| Economizer, Cold Out | 74 | 74.97 | 101.3 | 1.015 | 314 | 215.6 |  | 35
| Evaporator, Freshwater Steam Out | 75 | 74.97 | 38.56 | 7.682 | 2635 | 2403 | 1 | 0
| Evaporator, Brine Out | 76 | 76.39 | 38.56 | 1.032 | 319.9 | 221.1 | 0 | 85
Effect No.6 | Evaporator, Hot In | 80 | 74.97 | 38.56 | 7.682 | 2635 | 2403 | 1 | 0
| Evaporator, Hot Out | 81 | 74.97 | 38.56 | 1.895 | 620.2 | 504.2 | 0.132 | 0
| Economizer, Hot Out | 82 | 74.97 | 38.56 | 1.015 | 313.9 | 215.5 | 0 | 0
| Economizer, Cold In | 83 | 20 | 101.3 | 0.2965 | 84.01 | 0 |  | 35
| Economizer, Cold Out | 84 | 69.97 | 101.3 | 0.9548 | 293 | 195.8 |  | 35
| Evaporator, Freshwater Steam Out | 85 | 69.97 | 31.17 | 7.754 | 2626 | 2393 | 1 | 0
| Evaporator, Brine Out | 86 | 71.39 | 31.17 | 0.9721 | 298.9 | 201.4 | 0 | 85
Effect No.7 | Evaporator, Hot In | 90 | 69.97 | 31.17 | 7.754 | 2626 | 2393 | 1 | 0
| Evaporator, Hot Out | 91 | 69.97 | 31.17 | 1.769 | 572.4 | 458.9 | 0.1198 | 0
| Economizer, Hot Out | 92 | 69.97 | 31.17 | 0.9548 | 293 | 195.8 | 0 | 0
| Economizer, Cold In | 93 | 20 | 101.3 | 0.2965 | 84.01 | 0 |  | 35
| Economizer, Cold Out | 94 | 64.97 | 101.3 | 0.8933 | 272.1 | 176.1 |  | 35
| Evaporator, Freshwater Steam Out | 95 | 64.97 | 25.01 | 7.83 | 2617 | 2383 | 1 | 0
| Evaporator, Brine Out | 96 | 66.39 | 25.01 | 0.9108 | 277.9 | 181.6 | 0 | 85
Effect No.8 | Evaporator, Hot In | 100 | 64.97 | 25.01 | 7.83 | 2617 | 2383 | 1 | 0
| Evaporator, Hot Out | 101 | 64.97 | 25.01 | 1.638 | 523.9 | 413 | 0.1074 | 0
| Economizer, Hot Out | 102 | 64.97 | 25.01 | 0.8933 | 272 | 176.1 | 0 | 0
| Economizer, Cold In | 103 | 20 | 101.3 | 0.2965 | 84.01 | 0 |  | 35
| Economizer, Cold Out | 104 | 59.97 | 101.3 | 0.8309 | 251.1 | 156.4 |  | 35
| Evaporator, Freshwater Steam Out | 105 | 59.97 | 19.92 | 7.909 | 2609 | 2373 | 1 | 0
| Evaporator, Brine Out | 106 | 61.39 | 19.92 | 0.8487 | 257 | 161.9 | 0 | 85
Effect No.9 | Evaporator, Hot In | 110 | 59.97 | 19.92 | 7.909 | 2609 | 2373 | 1 | 0
| Evaporator, Hot Out | 111 | 59.97 | 19.92 | 1.502 | 474.5 | 366.4 | 0.09478 | 0
| Economizer, Hot Out | 112 | 59.97 | 19.92 | 0.831 | 251.1 | 156.4 | 0 | 0
| Economizer, Cold In | 113 | 20 | 101.3 | 0.2965 | 84.01 | 0 |  | 35
| Economizer, Cold Out | 114 | 54.97 | 101.3 | 0.7677 | 230.2 | 136.8 |  | 35
| Evaporator, Freshwater Steam Out | 115 | 54.97 | 15.74 | 7.99 | 2600 | 2362 | 1 | 0
| Evaporator, Brine Out | 116 | 56.39 | 15.74 | 0.7857 | 236.1 | 142.3 | 0 | 85
Effect No.10 | Evaporator, Hot In | 120 | 54.97 | 15.74 | 7.99 | 2600 | 2362 | 1 | 0
| Evaporator, Hot Out | 121 | 54.97 | 15.74 | 1.36 | 424.4 | 319.1 | 0.08196 | 0
| Economizer, Hot Out | 122 | 54.97 | 15.74 | 0.7677 | 230.2 | 136.7 | 0 | 0
| Economizer, Cold In | 123 | 20 | 101.3 | 0.2965 | 84.01 | 0 |  | 35
| Economizer, Cold Out | 124 | 49.97 | 101.3 | 0.7034 | 209.3 | 117.2 |  | 35
| Evaporator, Freshwater Steam Out | 125 | 49.97 | 12.34 | 8.075 | 2591 | 2352 | 1 | 0
| Evaporator, Brine Out | 126 | 51.39 | 12.34 | 0.7218 | 215.2 | 122.6 | 0 | 85
Effect No.11 | Evaporator, Hot In | 130 | 49.97 | 12.34 | 8.075 | 2591 | 2352 | 1 | 0
| Evaporator, Hot Out | 131 | 49.97 | 12.34 | 1.211 | 373.4 | 271.1 | 0.06891 | 0
| Economizer, Hot Out | 132 | 49.97 | 12.34 | 0.7035 | 209.2 | 117.1 | 0 | 0
| Economizer, Cold In | 133 | 20 | 101.3 | 0.2965 | 84.01 | 0 |  | 35
| Economizer, Cold Out | 134 | 44.97 | 101.3 | 0.6382 | 188.4 | 97.56 |  | 35
| Evaporator, Freshwater Steam Out | 135 | 44.97 | 9.583 | 8.164 | 2582 | 2341 | 1 | 0
| Evaporator, Brine Out | 136 | 46.39 | 9.583 | 0.6568 | 194.2 | 103 | 0 | 85
Effect No.12 | Evaporator, Hot In | 140 | 44.97 | 9.583 | 8.164 | 2582 | 2341 | 1 | 0
| Evaporator, Hot Out | 141 | 44.97 | 9.583 | 1.057 | 321.5 | 222.3 | 0.05562 | 0
| Economizer, Hot Out | 142 | 44.97 | 9.583 | 0.6383 | 188.3 | 97.49 | 0 | 0
| Economizer, Cold In | 143 | 20 | 101.3 | 0.2965 | 84.01 | 0 |  | 35
| Economizer, Cold Out | 144 | 39.97 | 101.3 | 0.572 | 167.5 | 77.99 |  | 35
| Evaporator, Freshwater Steam Out | 145 | 39.97 | 7.375 | 8.256 | 2573 | 2330 | 1 | 0
| Evaporator, Brine Out | 146 | 41.39 | 7.375 | 0.5909 | 173.3 | 83.45 | 0 | 85
Effect No.13 | Evaporator, Hot In | 150 | 39.97 | 7.375 | 8.256 | 2573 | 2330 | 1 | 0
| Evaporator, Hot Out | 151 | 39.97 | 7.375 | 0.8955 | 268.7 | 172.7 | 0.04209 | 0
| Economizer, Hot Out | 152 | 39.97 | 7.375 | 0.5721 | 167.4 | 77.91 | 0 | 0
| Economizer, Cold In | 153 | 20 | 101.3 | 0.2965 | 84.01 | 0 |  | 35
| Economizer, Cold Out | 154 | 34.97 | 101.3 | 0.5047 | 146.6 | 58.44 |  | 35
| Evaporator, Freshwater Steam Out | 155 | 34.97 | 5.621 | 8.352 | 2565 | 2319 | 1 | 0
| Evaporator, Brine Out | 156 | 36.39 | 5.621 | 0.5239 | 152.4 | 63.88 | 0 | 85
Effect No.14 | Evaporator, Hot In | 160 | 34.97 | 5.621 | 8.352 | 2565 | 2319 | 1 | 0
| Evaporator, Hot Out | 161 | 34.97 | 5.621 | 0.7269 | 215 | 122.4 | 0.02831 | 0
| Economizer, Hot Out | 162 | 34.97 | 5.621 | 0.5048 | 146.5 | 58.35 | 0 | 0
| Economizer, Cold In | 163 | 20 | 101.3 | 0.2965 | 84.01 | 0 |  | 35
| Economizer, Cold Out | 164 | 29.97 | 101.3 | 0.4364 | 125.7 | 38.91 |  | 35
| Evaporator, Freshwater Steam Out | 165 | 29.97 | 4.241 | 8.453 | 2555 | 2308 | 1 | 0
| Evaporator, Brine Out | 166 | 31.39 | 4.241 | 0.4559 | 131.5 | 44.35 | 0 | 85
Effect No.15 | Evaporator, Hot In | 170 | 29.97 | 4.241 | 8.453 | 2555 | 2308 | 1 | 0
| Evaporator, Hot Out | 171 | 29.97 | 4.241 | 0.5507 | 160.3 | 71.17 | 0.01426 | 0
| Economizer, Hot Out | 172 | 29.97 | 4.241 | 0.4364 | 125.6 | 38.82 | 0 | 0
| Economizer, Cold In | 173 | 20 | 101.3 | 0.2965 | 84.01 | 0 |  | 35
| Economizer, Cold Out | 174 | 24.97 | 101.3 | 0.3668 | 104.8 | 19.4 |  | 35
| Evaporator, Freshwater Steam Out | 175 | 24.97 | 3.165 | 8.557 | 2546 | 2297 | 1 | 0
| Evaporator, Brine Out | 176 | 26.39 | 3.165 | 0.3867 | 110.6 | 24.83 | 0 | 85
Condenser | Condenser, Hot In | 180 | 24.97 | 3.165 | 8.557 | 2546 | 2297 | 1 | 0
| Condenser, Hot Out | 181 | 24.97 | 3.165 | 0.3669 | 104.7 | 19.31 | 0 | 0
| Condenser, Cold In | 182 | 20 | 101.3 | 0.2965 | 84.01 | 0 |  | 35
| Condenser, Cold Out | 183 | 21.97 | 101.3 | 0.3245 | 92.27 | 7.698 |  | 35

## MED - Key Values
Region | T [C] | P [kPa] | m_dot_D [kg/s] | m_dot_B [kg/s] | m_dot_f [kg/s] | φ_D [kW] | φ_D_E [kW] | φ_D_B [kW] | φ_D_C [kW] | φ_D [kJ/kg] | φ_D_E [kJ/kg] | φ_D_B [kJ/kg] | φ_D_C [kJ/kg] | φ_D [%] | φ_D_E [%] | φ_D_B [%] | φ_D_C [%]
Effect No.1 | 94.97 | 84.53 | 1582 | 1108 | 2690 | 341512 | 8652 | 332860 |  | 303.6315 | 3.2164 | 300.4152 |  | 15.4306 | 20.7204 | 23.2373
Effect No.2 | 89.97 | 70.11 | 1290 | 902.7 | 2192.7 | 259923 | 6606 | 253317 |  | 283.6342 | 3.0127 | 280.6215 |  | 11.7442 | 15.8205 | 17.6843
Effect No.3 | 84.97 | 57.81 | 1066 | 746 | 1812 | 199649 | 5111 | 194538 |  | 263.5954 | 2.8206 | 260.7748 |  | 9.0208 | 12.2402 | 13.5809
Effect No.4 | 79.97 | 47.37 | 893.2 | 625.3 | 1518.5 | 154653 | 4008 | 150645 |  | 243.5558 | 2.6394 | 240.9164 |  | 6.9877 | 9.5986 | 10.5167
Effect No.5 | 74.97 | 38.56 | 759.2 | 531.4 | 1290.6 | 120703 | 3188 | 117515 |  | 223.6124 | 2.4702 | 221.1423 |  | 5.4538 | 7.6348 | 8.2038
Effect No.6 | 69.97 | 31.17 | 654.3 | 458 | 1112.3 | 94808 | 2573 | 92235 |  | 203.6997 | 2.3132 | 201.3865 |  | 4.2837 | 6.162 | 6.439
Effect No.7 | 64.97 | 25.01 | 571.9 | 400.4 | 972.3 | 74832 | 2110 | 72722 |  | 183.7935 | 2.1701 | 181.6234 |  | 3.3812 | 5.0532 | 5.0768
Effect No.8 | 59.97 | 19.92 | 507 | 354.9 | 861.9 | 59234 | 1759 | 57475 |  | 163.9879 | 2.0408 | 161.947 |  | 2.6764 | 4.2126 | 4.0124
Effect No.9 | 54.97 | 15.74 | 455.8 | 319.1 | 774.9 | 46891 | 1494 | 45397 |  | 144.1937 | 1.928 | 142.2657 |  | 2.1187 | 3.5779 | 3.1692
Effect No.10 | 49.97 | 12.34 | 415.6 | 290.9 | 706.5 | 36975 | 1294 | 35681 |  | 124.4888 | 1.8316 | 122.6573 |  | 1.6706 | 3.099 | 2.4909
Effect No.11 | 44.97 | 9.583 | 384.4 | 269.1 | 653.5 | 28867 | 1144 | 27723 |  | 104.7718 | 1.7506 | 103.0212 |  | 1.3043 | 2.7397 | 1.9354
Effect No.12 | 39.97 | 7.375 | 360.6 | 252.4 | 613 | 22100 | 1036 | 21064 |  | 85.1449 | 1.69 | 83.4548 |  | 0.99855 | 2.4811 | 1.4705
Effect No.13 | 34.97 | 5.621 | 343.2 | 240.2 | 583.4 | 16308.3 | 962.3 | 15346 |  | 65.5379 | 1.6495 | 63.8884 |  | 0.73686 | 2.3046 | 1.0713
Effect No.14 | 29.97 | 4.241 | 331.3 | 231.9 | 563.2 | 11200.9 | 917.9 | 10283 |  | 45.9722 | 1.6298 | 44.3424 |  | 0.50609 | 2.1983 | 0.71787
Effect No.15 | 24.97 | 3.165 | 324.4 | 227.1 | 551.5 | 6538.7 | 900.7 | 5638 |  | 26.4593 | 1.6332 | 24.8261 |  | 0.29544 | 2.1571 | 0.39359
Condenser | 24.97 | 3.165 | 324.4 |  |  | 739016 |  |  | 739016 | 2278.1011 |  |  | 2278.1011 | 33.3911 |  |  | 100
|  |  | m_dot_D [kg/s] | m_dot_B [kg/s] | m_dot_f [kg/s] | φ_D [kW] | φ_D_E [kW] | φ_D_B [kW] | φ_D_C [kW] | [5 empty] | φ_D_E [%] | φ_D_B [%] | φ_D_C [%]
|  | Total | 10263.3 | 6957.4 | 16896.3 | 2213210.9 | 41755.9 | 1432439 | 739016 | [5 empty] | 1.8867 | 64.7222 | 33.3911
5590.4
η_II | 0.4736 |  | m_dot_D [gal/s] | m_dot_B [gal/s] | m_dot_f [gal/s]
GOR_hv [kJ/kJ] | 5.212 |  | 2668.458 | 1808.924 | 4393.038
GOR_mass [kg/kg] | 4.329
Distillate Production [kg/kJ] | 0.0023105
Distillate Production [gal/kJ] | 0.00060073
Turbine Power [MW] | 1138
m_dot_npp [kg/s] | 2296 |  |  |  | 75 [
q_npp [kJ/kg] | 1935
Q_npp [MW] | 4442

## MED - Parameterization
T_0 [C] | m_dot_D [kg/s] | η_II | GOR_hv | GOR_steam | z_0 [g/kg] | m_dot_D [kg/s] | η_II | GOR_hv | GOR_steam | z_B [g/kg] | m_dot_D [kg/s] | η_II | GOR_hv | GOR_steam
20 | 9938 | 0.4736 | 5.212 | 4.329 | 5 | 14073 | 0.6191 | 7.411 | 6.129 | 50 | 5119 | 0.2822 | 2.662 | 2.23
18 | 9645 | 0.4822 | 5.056 | 4.201 | 10 | 13501 | 0.5996 | 7.106 | 5.88 | 60 | 7234 | 0.3704 | 3.779 | 3.151
16 | 9366 | 0.4901 | 4.907 | 4.079 | 15 | 12887 | 0.5785 | 6.78 | 5.613 | 70 | 8614 | 0.4241 | 4.51 | 3.752
14 | 9101 | 0.4975 | 4.766 | 3.964 | 20 | 12228 | 0.5556 | 6.429 | 5.326 | 80 | 9567 | 0.4599 | 5.015 | 4.167
12 | 8848 | 0.5043 | 4.631 | 3.854 | 25 | 11519 | 0.5306 | 6.052 | 5.017 | 90 | 10259 | 0.4854 | 5.382 | 4.468
10 | 8607 | 0.5106 | 4.503 | 3.749 | 30 | 10757 | 0.5034 | 5.647 | 4.685 | 100 | 10783 | 0.5044 | 5.661 | 4.697
8 | 8378 | 0.5165 | 4.381 | 3.649 | 35 | 9938 | 0.4736 | 5.212 | 4.329 | 110 | 11194 | 0.5191 | 5.879 | 4.875
6 | 8159 | 0.522 | 4.265 | 3.554 | 40 | 9059 | 0.441 | 4.746 | 3.946 | 120 | 11523 | 0.5308 | 6.054 | 5.019
4 | 7950 | 0.5272 | 4.154 | 3.463 | 45 | 8119 | 0.4052 | 4.247 | 3.536 | 130 | 11793 | 0.5404 | 6.198 | 5.137
2 | 7751 | 0.532 | 4.048 | 3.376 | 50 | 7118 | 0.3659 | 3.717 | 3.1 | 140 | 12019 | 0.5484 | 6.318 | 5.235

## SLTD
Region | Description | State Point | T [C] | P [kPa] | s [kJ/kg] | h [kJ/kg] | φ [kJ/kg] | x [-] | Salinity [g/kg] | Notes |  |  |  |  | 8190 | 2296
Evaporator No. 1 | Spray Evaporator, Brine In | 40 | 94.97 | 101.3 | 1.25 | 398 | 0 | - | 35 |  | Produced Steam Temperature [C] | Effect No. | Pressure [kPa] | Distilled Water Mass Flow Rate [kg/s] | Percentage of Total Distilled Water Mass Flow Rate [%] | Distilled Water Mass Flow Rate over NPP Mass Flow Rate [kg/s] | Salinity [ppt] | Exergy Destroyed by Evaporator [kW]
| Spray Evaporator, Pump Ideal | 41 | 94.97 | 106.4 | 1.25 | 398 | 0.005266 | - | 35 |  | 92.97 | 1 | 78.49 | 1438 | 0.17558 | 0.62631 | 38.89 | 297809.8
| Spray Evaporator, Pump Real | 42 | 94.97 | 106.4 | 1.25 | 617 | 0.006145 | - | 35 |  | 90.98 | 2 | 72.82 | 1294 | 0.158 | 0.56359 | 43.21 | 268505
| Liquid Brine Out | 43 | 92.97 | 78.49 | 1.849 | 617 | 207.1 | 0.1 | 38.89 |  | 88.98 | 3 | 67.5 | 1165 | 0.14225 | 0.5074 | 48.01 | 242203.5
| Freshwater Steam Out | 44 | 92.97 | 78.49 | 7.44 | 2664 | 1935 | 1 | 0 |  | 86.98 | 4 | 62.5 | 1048 | 0.12796 | 0.45645 | 53.35 | 218403.2
| Condensed Freshwater | 45 | 92.97 | 78.49 | 1.227 | 389.6 | -2151 | 0 | 0 |  | 84.98 | 5 | 57.82 | 943.5 | 0.1152 | 0.41093 | 59.27 | 197002.8
Evaporator No. 2 | Spray Evaporator, Brine In | 50 | 92.97 | 78.49 | 1.227 | 389.6 | 0 | 0 | 38.89 |  | 82.98 | 6 | 53.43 | 849.1 | 0.10368 | 0.36982 | 65.86 | 177631.72
| Spray Evaporator, Pump Ideal | 51 | 92.98 | 82.42 | 1.227 | 389.6 | 0.004066 | - | 38.89 |  | 80.98 | 7 | 49.33 | 764.2 | 0.093309 | 0.33284 | 73.18 | 160176.32
| Spray Evaporator, Pump Real | 52 | 92.98 | 82.42 | 1.227 | 389.6 | 0.004745 | - | 38.89 |  | 78.98 | 8 | 45.49 | 687.8 | 0.08398 | 0.29956 | 81.31 | 144438
| Liquid Brine Out | 53 | 90.98 | 72.82 | 1.83 | 609.1 | 207.5 | 0.1 | 43.21
| Freshwater Steam Out | 54 | 90.98 | 72.82 | 7.466 | 2661 | 1939 | 1 | 0
| Condensed Freshwater | 55 | 90.98 | 72.82 | 1.204 | 381.1 | -2155 | 0 | 0
Evaporator No. 3 | Spray Evaporator, Brine In | 60 | 90.98 | 72.82 | 1.204 | 381.1 | 0 | 0 | 43.21
| Spray Evaporator, Pump Ideal | 61 | 90.98 | 76.47 | 1.204 | 381.2 | 0.003766 | - | 43.21
| Spray Evaporator, Pump Real | 62 | 90.98 | 76.47 | 1.204 | 381.2 | 0.004395 | - | 43.21
| Liquid Brine Out | 63 | 88.98 | 67.5 | 1.812 | 601.3 | 207.9 | 0.1 | 48.01
| Freshwater Steam Out | 64 | 88.98 | 67.5 | 7.491 | 2658 | 1943 | 1 | 0
| Condensed Freshwater | 65 | 88.98 | 67.5 | 1.181 | 372.7 | -2159 | 0 | 0
Evaporator No. 4 | Spray Evaporator, Brine In | 70 | 88.98 | 67.5 | 1.181 | 372.7 | 0 | 0 | 48.01
| Spray Evaporator, Pump Ideal | 71 | 88.98 | 70.87 | 1.181 | 372.7 | 0.003486 | - | 48.01
| Spray Evaporator, Pump Real | 72 | 88.98 | 70.87 | 1.181 | 372.7 | 0.004067 | - | 48.01
| Liquid Brine Out | 73 | 86.98 | 62.5 | 1.794 | 593.4 | 208.4 | 0.1 | 53.35
| Freshwater Steam Out | 74 | 86.98 | 62.5 | 7.517 | 2655 | 1947 | 1 | 0
| Condensed Freshwater | 75 | 86.98 | 62.5 | 1.158 | 364.3 | -2163 | 0 | 0
Evaporator No. 5 | Spray Evaporator, Brine In | 80 | 86.98 | 62.5 | 1.158 | 364.3 | 0 | 0 | 53.35
| Spray Evaporator, Pump Ideal | 81 | 86.98 | 65.63 | 1.158 | 364.3 | 0.003222 | - | 53.35
| Spray Evaporator, Pump Real | 82 | 86.98 | 65.63 | 1.158 | 364.3 | 0.00376 | - | 53.35
| Liquid Brine Out | 83 | 84.98 | 57.82 | 1.775 | 585.5 | 208.8 | 0.1 | 59.27
| Freshwater Steam Out | 84 | 84.98 | 57.82 | 7.544 | 2651 | 1950 | 1 | 0
| Condensed Freshwater | 85 | 84.98 | 57.82 | 1.134 | 355.9 | -2167 | 0 | 0
Evaporator No. 6 | Spray Evaporator, Brine In | 90 | 84.98 | 57.82 | 1.134 | 355.9 | 0 | 0 | 59.27
| Spray Evaporator, Pump Ideal | 91 | 84.98 | 60.71 | 1.134 | 355.9 | 0.002976 | - | 59.27
| Spray Evaporator, Pump Real | 92 | 84.98 | 60.71 | 1.134 | 355.9 | 0.003473 | - | 59.27
| Liquid Brine Out | 93 | 82.98 | 53.43 | 1.757 | 577.6 | 209.2 | 0.1 | 65.86
| Freshwater Steam Out | 94 | 82.98 | 53.43 | 7.57 | 2648 | 1954 | 1 | 0
| Condensed Freshwater | 95 | 82.98 | 53.43 | 1.111 | 347.5 | -2171 | 0 | 0
Evaporator No. 7 | Spray Evaporator, Brine In | 100 | 82.98 | 53.43 | 1.111 | 347.5 | 0 | 0 | 65.86
| Spray Evaporator, Pump Ideal | 101 | 82.98 | 56.11 | 1.111 | 347.5 | 0.002746 |  | 65.86
| Spray Evaporator, Pump Real | 102 | 82.98 | 56.11 | 1.111 | 347.5 | 0.003204 |  | 65.86
| Liquid Brine Out | 103 | 80.98 | 49.33 | 1.738 | 569.7 | 209.6 | 0.1 | 73.18
| Freshwater Steam Out | 104 | 80.98 | 49.33 | 7.598 | 2645 | 1958 | 1 | 0
| Condensed Freshwater | 105 | 80.98 | 49.33 | 1.087 | 339.1 | -2175 | 0 | 0
Evaporator No. 8 | Spray Evaporator, Brine In | 110 | 80.98 | 49.33 | 1.087 | 339.1 |  | 0 | 73.18
| Spray Evaporator, Pump Ideal | 111 | 80.98 | 51.8 | 1.087 | 339.1 | 0.002531 | - | 73.18
| Spray Evaporator, Pump Real | 112 | 80.98 | 51.8 | 1.087 | 339.1 | 0.002953 | - | 73.18
| Liquid Brine Out | 113 | 78.98 | 45.49 | 1.72 | 561.8 | 210 | 0.1 | 81.31
| Freshwater Steam Out | 114 | 78.98 | 45.49 | 7.625 | 2641 | 1961 | 1 | 0
| Condensed Freshwater | 115 | 78.98 | 45.49 | 1.063 | 330.7 | -2179 | 0 | 0
Condenser Series | Condenser No. 1 | 120 | 25.76 | 101.3 | 0.3779 | 108.1 | - | 0 | 0
| Condenser No. 2 | 121 | 32.16 | 101.3 | 0.4664 | 134.8 | - | 0 | 0
| Condenser No. 3 | 122 | 39.25 | 101.3 | 0.5623 | 164.5 | - | 0 | 0
| Condenser No. 4 | 123 | 47.11 | 101.3 | 0.6662 | 197.3 | - | 0 | 0
| Condenser No. 5 | 124 | 55.82 | 101.3 | 0.7784 | 233.8 | - | 0 | 0
| Condenser No. 6 | 125 | 65.47 | 101.3 | 0.8994 | 274.1 | - | 0 | 0
| Condenser No. 7 | 126 | 76.15 | 101.3 | 1.03 | 318.9 | - | 0 | 0
| Condenser No. 8 | 127 | 87.97 | 101.3 | 0.3779 | 368.5 | - | 0 | 0
Brine Outflow | Outlet | 130 | 78.98 | 45.49 | 1.72 | 561.8 | - | 0 | 81.31

## SLTD Key Values
Evaporator | Brine Flow Rate [kg/s] | Distillate Flow Rate [kg/s]
1 | 12942 | 1438
2 | 11648 | 1294
3 | 10483 | 1165
4 | 9435 | 1048
5 | 8491 | 943.5
6 | 7642 | 849.1
7 | 6878 | 764.2
8 | 6190 | 687.8
Total | 6190 | 8190
m_dot_c = 65,917 [kg/s] |  |  | NPP Specificatations are Identical between SLTD and MED
m_dot_f = 14,380 [kg/s]
GOR = 4.1 [hv] | GOR = 3.567 [kg]
Distillate Production = 0.007197 [kg/kJ]
Second Law Efficiency = 45.83%

## SLTD - Parameterization
T_0 | GOR_mass | GOR_hv | m_dot_f | m_dot_B | m_dot_D | Allowable Salinity | eta_ii | E | m_dot_B | m_dot_D | m_dot_f | Allowable Salinity | GOR_mass | GOR_hv | eta_ii
[C] |  |  | [kg/s] | [kg/s] | [kg/s] | [ppt] |  |  | [kg/s] | [kg/s] | [kg/s] | [ppt]
2 | 2.875 | 3.283 | 11592 | 4990 | 6602 | 81.31 | 0.4332 | 0.01 | 13269 | 1111 | 14380 | 37.93 | 0.4839 | 0.5561 | 0.9824
4 | 2.939 | 3.36 | 11848 | 5100 | 6748 | 81.31 | 0.4359 | 0.02263 | 11974 | 2406 | 14380 | 42.03 | 1.048 | 1.205 | 0.8865
6 | 3.005 | 3.439 | 12116 | 5215 | 6900 | 81.31 | 0.4387 | 0.03526 | 10790 | 3590 | 14380 | 46.64 | 1.563 | 1.797 | 0.7989
8 | 3.075 | 3.522 | 12395 | 5336 | 7059 | 81.31 | 0.4414 | 0.04789 | 9710 | 4670 | 14380 | 51.83 | 2.034 | 2.337 | 0.7189
10 | 3.147 | 3.608 | 12687 | 5461 | 7226 | 81.31 | 0.4442 | 0.06053 | 8726 | 5654 | 14380 | 57.68 | 2.462 | 2.83 | 0.6461
12 | 3.223 | 3.697 | 12994 | 5593 | 7400 | 81.31 | 0.447 | 0.07316 | 7831 | 6549 | 14380 | 64.27 | 2.852 | 3.278 | 0.5798
14 | 3.303 | 3.791 | 13315 | 5732 | 7583 | 81.31 | 0.4498 | 0.08579 | 7017 | 7363 | 14380 | 71.73 | 3.207 | 3.686 | 0.5195
16 | 3.386 | 3.889 | 13652 | 5877 | 7775 | 81.31 | 0.4526 | 0.09842 | 6277 | 8102 | 14380 | 80.17 | 3.529 | 4.056 | 0.4648
18 | 3.474 | 3.992 | 14007 | 6029 | 7977 | 81.31 | 0.4554 | 0.1111 | 5607 | 8772 | 14380 | 89.76 | 3.821 | 4.391 | 0.4152
20 | 3.567 | 4.1 | 14380 | 6190 | 8190 | 81.31 | 0.4583 | 0.1237 | 5001 | 9379 | 14380 | 100.6 | 4.085 | 4.695 | 0.3703
22 | 3.665 | 4.213 | 14774 | 6360 | 8414 | 81.31 | 0.4612 | 0.1363 | 4452 | 9927 | 14380 | 113 | 4.324 | 4.969 | 0.3297
24 | 3.768 | 4.333 | 15189 | 6538 | 8651 | 81.31 | 0.4641 | 0.1489 | 3957 | 10423 | 14380 | 127.2 | 4.539 | 5.217 | 0.293
26 | 3.877 | 4.459 | 15629 | 6728 | 8901 | 81.31 | 0.467 | 0.1616 | 3511 | 10869 | 14380 | 143.3 | 4.734 | 5.44 | 0.26
28 | 3.992 | 4.593 | 16095 | 6928 | 9166 | 81.31 | 0.4699 | 0.1742 | 3110 | 11270 | 14380 | 161.9 | 4.909 | 5.641 | 0.2302
30 | 4.115 | 4.735 | 16589 | 7141 | 9448 | 81.31 | 0.4729 | 0.1868 | 2749 | 11631 | 14380 | 183.1 | 5.066 | 5.822 | 0.2035
32 | 4.245 | 4.886 | 17115 | 7367 | 9747 | 81.31 | 0.4758 | 0.1995 | 2425 | 11955 | 14380 | 207.5 | 5.207 | 5.984 | 0.1796
34 | 4.384 | 5.047 | 17675 | 7608 | 10066 | 81.31 | 0.4788 | 0.2121 | 2136 | 12244 | 14380 | 235.7 | 5.333 | 6.129 | 0.1581
36 | 4.533 | 5.218 | 18273 | 7866 | 10407 | 81.31 | 0.4818 | 0.2247 | 1876 | 12503 | 14380 | 268.2 | 5.446 | 6.259 | 0.1389
38 | 4.691 | 5.401 | 18912 | 8141 | 10771 | 81.31 | 0.4848 | 0.2374 | 1645 | 12734 | 14380 | 305.9 | 5.546 | 6.374 | 0.1218
40 | 4.862 | 5.597 | 19599 | 8437 | 11162 | 81.31 | 0.4879 | 0.25 | 1440 | 12940 | 14380 | 349.6 | 5.636 | 6.477 | 0.1066

## LCOW_Inputs
LCOW Inputs |  | Technical Inputs
NOTE: A8/B8, A15/B15, A16/B16, A19/B19, 20, 21, 22, 23, 24, 25, are all assumptions/placeholders
Base distillate mass flow (kg/s) | 10263.3
Water density (kg/m^3) | 1000
Base water production (m^3/s) | 10.2633
Base water production (m^3/day) | 886749.12
Capacity factor of desal plant (-) | 0.9
Annual water production (m^3/yr) | 291297085.9
Distillate production (kg/kJ) | 0.0023105
Heat per kg water (kJ/kg) | 432.8043
Heat per m^3 water (kWh_th/m^3) | 120.2234
Economic Inputs
Plant lifetime (years) | 25
Discount rate (fraction) | 0.07
Capital recovery factor CRF (-) | 0.085811
Base plant capacity (m^3/day) | 886749.12
Base CAPEX (total, $) | 800000000
Fixed O&M fraction of CAPEX (1/yr) | 0.03
Variable O&M non-energy ($/m^3) | 0.2
Specific electricity use (kWh/m^3) | 1.5
Electricity price ($/kWh) | 0.07
Thermal energy price ($/kWh_th) | 0 | (Treating waste heat as free)
CAPEX scaling exponent alpha (-) | 0.7
Note on thermal energy cost | Waste heat from NPP condenser treated as zero-cost thermal energy
RO Inputs
RO base plant capacity (m^3/day) | 886749.12 |  | Note: Want RO to have the same capacity as the MED plant for fair comparison.
RO CAPEX per capacity ($/(m^3/day)) | 1200 |  | Note: Placeholder
RO CAPEX base (total, $) | 1064098944
RO Fixed O&M fraction (1/yr) | 0.03
RO Variable O&M non-energy ($/m^3) | 0.15
RO Specific electricity use (kWh/m^3) | 3.5
RO Electricity price ($/kWh) | 0.07
RO Capacity factor (-) | 0.9
RO annual water production (m^3/yr) | 291297085.9

## LCOW_Base
Base-case LCOW (MED + nuclear waste heat)
Annual water production (m^3/yr) | 291297085.9
Annualized CAPEX ($/yr) | 68648413.78 |  | CAPEX per m^3 | 0.23566
Fixed O&M ($/yr) | 24000000 |  | Fixed O&M per m^3 | 0.08239
Variable O&M non-energy ($/yr) | 58259417.18 |  | Var O&M per m^3 | 0.2
Electricity cost ($/yr) | 30586194.02 |  | Electricity per m^3 | 0.105
Thermal energy cost ($/yr) | 0 |  | Thermal Energy Cost per m^3 | 0
Total annual cost ($/yr) | 181494025 |  | LCOW | 0.62305
LCOW ($/m^3) | 0.62305
| CAPEX | Fixed O&M | Var O&M | Electricity | Total
MED | 0.23566 | 0.08239 | 0.2 | 0.105 | 0.62305
RO | 0.31346 | 0.10959 | 0.15 | 0.245 | 0.82

## LCOW_Param_MED
T_0 [C] | m_dot_D [kg/s] | GOR_hv | Water prod (m^3/day) | Annual water (m^3/yr) | Scaled CAPEX ($) | Annualized CAPEX ($/yr) | Fixed O&M ($/yr) | Variable O&M non-energy ($/yr) | Electricity cost ($/yr) | Thermal energy cost ($/yr) | Total annual cost ($/yr) | LCOW ($/m^3) | CAPEX ($/m^3) | Fixed O&M ($/m^3) | Var O&M ($/m^3) | Electricity ($/m^3)
20 | 9938 | 5.212 | 858643.2 | 282064291.2 | 782164976 | 67117981.14 | 23464949.28 | 56412858.24 | 29616750.58 | 0 | 176612539.2 | 0.62614 | 0.23795 | 0.08319 | 0.2 | 0.105
18 | 9645 | 5.056 | 833328 | 273748248 | 765950374.4 | 65726597.8 | 22978511.23 | 54749649.6 | 28743566.04 | 0 | 172198324.7 | 0.62904 | 0.2401 | 0.08394 | 0.2 | 0.105
16 | 9366 | 4.907 | 809222.4 | 265829558.4 | 750372618.2 | 64389862.47 | 22511178.55 | 53165911.68 | 27912103.63 | 0 | 167979056.3 | 0.63191 | 0.24222 | 0.084683 | 0.2 | 0.105
14 | 9101 | 4.766 | 786326.4 | 258308222.4 | 735447118.1 | 63109097.59 | 22063413.54 | 51661644.48 | 27122363.35 | 0 | 163956519 | 0.63473 | 0.24432 | 0.085415 | 0.2 | 0.105
12 | 8848 | 4.631 | 764467.2 | 251127475.2 | 721075351.3 | 61875848.85 | 21632260.54 | 50225495.04 | 26368384.9 | 0 | 160101989.3 | 0.63753 | 0.24639 | 0.086141 | 0.2 | 0.105
10 | 8607 | 4.503 | 743644.8 | 244287316.8 | 707270155.2 | 60691217.84 | 21218104.66 | 48857463.36 | 25650168.26 | 0 | 156416954.1 | 0.6403 | 0.24844 | 0.086857 | 0.2 | 0.105
8 | 8378 | 4.381 | 723859.2 | 237787747.2 | 694044504.3 | 59556317.88 | 20821335.13 | 47557549.44 | 24967713.46 | 0 | 152902915.9 | 0.64302 | 0.25046 | 0.087563 | 0.2 | 0.105
6 | 8159 | 4.265 | 704937.6 | 231572001.6 | 681294563.8 | 58462238.9 | 20438836.91 | 46314400.32 | 24315060.17 | 0 | 149530536.3 | 0.64572 | 0.25246 | 0.088261 | 0.2 | 0.105
4 | 7950 | 4.154 | 686880 | 225640080 | 669030721 | 57409872.21 | 20070921.63 | 45128016 | 23692208.4 | 0 | 146301018.2 | 0.64838 | 0.25443 | 0.088951 | 0.2 | 0.105
2 | 7751 | 4.048 | 669686.4 | 219991982.4 | 657263456.2 | 56400117.13 | 19717903.69 | 43998396.48 | 23099158.15 | 0 | 143215575.5 | 0.651 | 0.25637 | 0.08963 | 0.2 | 0.105

## LCOW_RO
Reference LCOW (RO desalination)
Annual water production (m^3/yr) | 291297085.9
Annualized CAPEX ($/yr) | 91310880.76
Fixed O&M ($/yr) | 31922968.32
Variable O&M non-energy ($/yr) | 43694562.89
Electricity cost ($/yr) | 71367786.05
Total annual cost ($/yr) | 238296198
LCOW ($/m^3) | 0.81805
CAPEX $/m^3 | 0.31346
Fixed O&M $/m^3 | 0.10959
Var O/M $/m^3 | 0.15
Electricity $/m^3 | 0.245
LCOW_RO | 0.81805